## IO List
Glass Furnace 1: IO List
PM-MLT-F1-FDS-001 Rev A, attachment. Furnace PLC: Modbus TCP 192.168.10.20 (reference only, not configured in this build).
Tag | Description | Signal | Unit | Range | PLC Address (reference) | Source | Sim Min | Sim Max | Initial Value | Alarm | Alarm Priority | Historian
Plant_Manila/Melting_Area/Glass_Furnace_1/North_Burners/North_Burner_1.ValveOpening | North Burner 1 control valve opening | AI | % | 0-100 | HR 40001 | Simulated | 62 | 70 | 66 |  |  | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/North_Burners/North_Burner_1.OilFlow | North Burner 1 oil flow | AI | kg/h | 0-300 | HR 40002 | Simulated | 212 | 226 | 219 |  |  | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/North_Burners/North_Burner_2.ValveOpening | North Burner 2 control valve opening | AI | % | 0-100 | HR 40003 | Simulated | 64 | 72 | 68 |  |  | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/North_Burners/North_Burner_2.OilFlow | North Burner 2 oil flow | AI | kg/h | 0-300 | HR 40004 | Simulated | 210 | 228 | 219 |  |  | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/North_Burners/North_Burner_3.ValveOpening | North Burner 3 control valve opening | AI | % | 0-100 | HR 40005 | Simulated | 60 | 68 | 64 |  |  | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/North_Burners/North_Burner_3.OilFlow | North Burner 3 oil flow | AI | kg/h | 0-300 | HR 40006 | Simulated | 214 | 224 | 219 |  |  | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/North_Burners/North_Burner_4.ValveOpening | North Burner 4 control valve opening | AI | % | 0-100 | HR 40007 | Simulated | 63 | 71 | 67 |  |  | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/North_Burners/North_Burner_4.OilFlow | North Burner 4 oil flow | AI | kg/h | 0-300 | HR 40008 | Simulated | 211 | 227 | 219 |  |  | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/South_Burners/South_Burner_1.ValveOpening | South Burner 1 control valve opening | AI | % | 0-100 | HR 40009 | Simulated | 61 | 69 | 65 |  |  | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/South_Burners/South_Burner_1.OilFlow | South Burner 1 oil flow | AI | kg/h | 0-300 | HR 40010 | Simulated | 213 | 225 | 219 |  |  | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/South_Burners/South_Burner_2.ValveOpening | South Burner 2 control valve opening | AI | % | 0-100 | HR 40011 | Simulated | 65 | 73 | 69 |  |  | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/South_Burners/South_Burner_2.OilFlow | South Burner 2 oil flow | AI | kg/h | 0-300 | HR 40012 | Simulated | 209 | 229 | 219 |  |  | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/South_Burners/South_Burner_3.ValveOpening | South Burner 3 control valve opening | AI | % | 0-100 | HR 40013 | Simulated | 64 | 72 | 68 |  |  | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/South_Burners/South_Burner_3.OilFlow | South Burner 3 oil flow | AI | kg/h | 0-300 | HR 40014 | Simulated | 210 | 226 | 218 |  |  | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/South_Burners/South_Burner_4.ValveOpening | South Burner 4 control valve opening | AI | % | 0-100 | HR 40015 | Simulated | 62 | 70 | 66 |  |  | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/South_Burners/South_Burner_4.OilFlow | South Burner 4 oil flow | AI | kg/h | 0-300 | HR 40016 | Simulated | 212 | 226 | 219 |  |  | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/BurnerFlowSetpoint | Oil flow setpoint, all burners | AO | kg/h | 0-300 | HR 40017 | Operator |  |  | 220 |  |  | No
Plant_Manila/Melting_Area/Glass_Furnace_1/CrownTemperature | Furnace crown temperature | AI | °C | 0-1800 | HR 40018 | Simulated | 1545 | 1565 | 1555 | Hi 1580 / HiHi 1600 | Warning / Critical | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/GlassLevel | Molten glass level | AI | mm | 0-2000 | HR 40019 | Simulated | 1195 | 1205 | 1200 | Lo 1180 | Warning | Yes
Plant_Manila/Melting_Area/Glass_Furnace_1/OilHeaderPressure | Fuel oil supply header pressure | AI | kPa | 0-1200 | HR 40020 | Simulated | 800 | 840 | 820 | Lo 700 | Warning | Yes